Lightning
A Lightning Talk
Nigel Titley

---
What is it?
- Electrical discharge: IC, CC or GC
- Collision of light and heavy ice particles combined with updraughts
- 100,000 amps (typical)
- 0.2 seconds (typical)
- Top of cloud +ve, bottom of cloud -ve
- GC is what concerns us.

---
How does it work

---
What does it look like?

---
Threat to Life
- Not very high (24,000 deaths annually worldwide)
- Mortality rate about 10% - 20%
- Direct hits mostly fatal but rare
- Trees and damp masonry explode
- Ground currents can choose foot – foot discharge path

---
Odd burn marks

---
Protection
- Lightning rod
  - Increases chance of hit
  - Conducts current to ground
  - Must have low resistance and low impedance
  - Conductor should be as straight as possible
  - IEC 62305 for assessing risk

---
Electronics Effects
- Induced currents normally cause damage
- Typical 1KV exponential pulse, 1 ms duration, 10 µs rise time
- Increased porosity in underground cables causing failure later
- Reciprocal law (1KV once a year, 500V twice a year etc)

---
Electronics Protection
- Surge arrestor
  - Gas discharge + avalanche diode
    - Limited life
    - Slow to act
    - Fail to open circuit
  - Metal Oxide Varistor (MOV)
    - Limited life
    - Fail to short circuit (catch fire)
    - Combine with slow-blow fuse

---
Economics
- If device is cheap then don't bother with protection (phones)
- If device is expensive then lightning protection may be worth it (data centre)
- Insurance may depend on lightning protection (churches)
- Plant trees

---
Advice
- Stay inside
- Use “flash-boom” test (5 seconds per mile)
- If storm is less than 5 miles away then take precautions
- Stay indoors until 30 mins after last thunder heard

---
Questions?